EXAMPLE DOCUMENT. Dralenko Kitchens Manufacturing (Pty) Ltd is a fictitious company. Every company, person, address, date, figure and reference number in this example is made up; only the Care Net letterhead and any public emergency number are real. For guidance only; not a document to sign or rely on.

Example for a Health and Safety File, Section F: Registers and inspections

# Ladder and Portable Electrical Equipment Inspection Register

Dralenko Kitchens Manufacturing, Hamilton factory, Bloemfontein. Register for the second quarter of 2026

| About this example | Detail |
| --- | --- |
| Company in the example | Dralenko Kitchens Manufacturing (Pty) Ltd, a fictitious company |
| Where it is filed | Section F: Registers and inspections |
| Published by | Care Net Consultants, as guidance for companies building a Health and Safety File |

## How to use this example

This example shows the form and content Care Net recommends for this document in a Health and Safety File. Adapt it to your company, your sites and your appointments; your registered Health and Safety practitioner confirms it before your File is released. Not legal advice.

## Contents

1. Register details

2. How the register works

3. Monthly inspection rounds

4. Ladders: exceptions and sample entries

5. Portable electrical equipment: exceptions and sample entries

6. Review

# Ladder and Portable Electrical Equipment Inspection Register

Dralenko Kitchens Manufacturing, Hamilton factory, Bloemfontein. Register for the second quarter of 2026

## 1. Register details

| Item | Detail |
| --- | --- |
| Site | Hamilton factory, 14 Kiewiet Street, Hamilton, Bloemfontein (fictitious address) |
| Equipment covered | Portable ladders and step ladders; portable electrical tools and extension leads used in the workshop and assembly bays |
| Appointed inspector | Pieter Botha, Maintenance Supervisor, appointed in writing as the competent person for ladders and portable electrical equipment (appointment letter in Section B) |
| Inspection interval | Monthly, as the company's risk assessment sets, and before first use of any new or repaired item |
| Register kept by | Naledi Mokoena, Health and Safety Officer |

## 2. How the register works

- Every ladder and portable electrical item carries a unique number and a coloured inspection tag for the current month.

- The inspector checks each item against the checklist for its type and records the result below on the day.

- An item that fails is tagged Do not use, removed to the locked quarantine cage and recorded as an action until it is repaired or destroyed.

- The Health and Safety Officer reviews the register monthly and reports open actions to the health and safety committee.

## 3. Monthly inspection rounds

Every ladder and portable electrical item in use was inspected on each monthly round. The round sheets, one line per item for each round, are filed behind this register.

| Round | Ladders inspected | Portable electrical items inspected | Every item in use inspected |
| --- | --- | --- | --- |
| 06/04/2026 | 6 of 6 (LAD 01 to LAD 06) | 17 of 17 (PE 01 to PE 17) | Yes |
| 04/05/2026 | 6 of 6 (LAD 03 replaced by LAD 07) | 17 of 17 | Yes |
| 01/06/2026 | 6 of 6 | 17 of 17; one untagged item found and removed (PE 18) | Yes |

## 4. Ladders: exceptions and sample entries

An extract from the round sheets: every failure, repair and new item, with a sample of the passed entries.

| Date | Item no. | Description | By | Findings | Action and status |
| --- | --- | --- | --- | --- | --- |
| 06/04/2026 | LAD 01 | Aluminium step ladder, 6 treads, assembly bay | P. Botha | Good condition; feet and locking stays intact | None. Green tag fitted |
| 06/04/2026 | LAD 02 | Fibreglass extension ladder, 3,6 m, maintenance store | P. Botha | One rubber foot worn through | Tagged Do not use; foot replaced 08/04/2026; reinspected and passed 08/04/2026. Closed |
| 06/04/2026 | LAD 03 | Wooden step ladder, paint store | P. Botha | Split in rear stile; not repairable | Destroyed 07/04/2026; replaced with LAD 07 (fibreglass). Closed |
| 04/05/2026 | LAD 01 | Aluminium step ladder, assembly bay | P. Botha | Good condition | None. Yellow tag fitted |
| 04/05/2026 | LAD 07 | Fibreglass step ladder, paint store (new) | P. Botha | Inspected before first use; good condition | Entered in register. Closed |
| 01/06/2026 | LAD 02 | Fibreglass extension ladder, maintenance store | P. Botha | Good condition; label legible | None. Blue tag fitted |

## 5. Portable electrical equipment: exceptions and sample entries

| Date | Item no. | Description | By | Findings | Action and status |
| --- | --- | --- | --- | --- | --- |
| 06/04/2026 | PE 04 | Angle grinder, 115 mm, workshop | P. Botha | Casing sound; plug and cable good; guard fitted | None. Green tag fitted |
| 06/04/2026 | PE 09 | Extension lead, 20 m, assembly bay | P. Botha | Cable sheath cut near the plug; inner cores visible | Tagged Do not use; lead shortened and new plug fitted by the electrician 09/04/2026; reinspected and passed. Closed |
| 06/04/2026 | PE 12 | Portable drill, assembly bay | P. Botha | Trigger switch sticks | Removed from use; sent for repair 07/04/2026; returned and passed 21/04/2026. Closed |
| 04/05/2026 | PE 15 | Mobile earth leakage unit, workshop | P. Botha | Test button trips the unit correctly | None. Yellow tag fitted |
| 01/06/2026 | PE 09 | Extension lead, 18 m after repair | P. Botha | Good condition | None. Blue tag fitted |
| 01/06/2026 | PE 18 | Heat gun, paint store | P. Botha | No inspection tag; item brought from home by an employee | Removed from site 01/06/2026; toolbox talk on personal tools held 02/06/2026. Closed |

## 6. Review

Quarter summary: three monthly rounds, on 06/04, 04/05 and 01/06/2026, each covering every ladder and portable electrical item in use: 69 inspections in all (23 items on each round), plus the reinspections after repair and before first use. Four items failed and one untagged item was found and removed; all five actions were closed, the April actions by 21/04/2026 and the June action on the day it was found. No open actions at the end of June 2026. Reported to the health and safety committee meeting of 09/07/2026.

______________________________

Appointed inspector

Pieter Botha, Date: 01/07/2026

______________________________

Health and Safety Officer (register reviewed)

Naledi Mokoena, Date: 03/07/2026

End of the example. The company, people and records in it are fictitious; the cover page explains how to use it.